#

#	In nagios it was follow two UPS’es.

[root@vm-vol-nag4-tst objects]# ls -1 ups/PL-01-UPS1-Eaton.cfg ups/PL-04-UPS1-Eaton.cfg

ups/PL-01-UPS1-Eaton.cfg

ups/PL-04-UPS1-Eaton.cfg

[root@vm-vol-nag4-tst objects]#

[root@vm-vol-nag4-tst servers]# /usr/local/nagios/libexec/check_snmp -H 172.18.98.2 -o .1.3.6.1.4.1.534.1.3.4.1.2.1 -C tcspub_123 -c200:

SNMP OK - 231 | iso.3.6.1.4.1.534.1.3.4.1.2.1=231

[root@vm-vol-nag4-tst servers]#

#

#	Before snmp options on UPS was properly configured - I had absence fo connection.

[root@vm-vol-nag4-tst servers]# /usr/local/nagios/libexec/check_snmp -H 172.18.98.4 -o .1.3.6.1.4.1.534.1.3.4.1.2.1 -C tcspub_123 -c200:

External command error: Timeout: No Response from 172.18.98.4:161.

[root@vm-vol-nag4-tst servers]#

[root@vm-vol-nag4-tst servers]# snmpwalk -v 1 -c tcspub_123 172.18.98.2 . | head

SNMPv2-MIB::sysDescr.0 = STRING: Linux PowerXpert-00-20-85-F1-2E-14 3.2.2 #1 PREEMPT Wed Oct 14 09:39:43 CEST 2015 ppc

SNMPv2-MIB::sysObjectID.0 = OID: SNMPv2-SMI::enterprises.534.2.12

DISMAN-EVENT-MIB::sysUpTimeInstance = Timeticks: (139197265) 16 days, 2:39:32.65

SNMPv2-MIB::sysContact.0 = STRING: Vladislav Lesoviy

SNMPv2-MIB::sysName.0 = STRING: PowerXpert-00-20-85-F1-2E-14

SNMPv2-MIB::sysLocation.0 = STRING: MSK Polkovaya 2 Floor 1

SNMPv2-MIB::sysORLastChange.0 = Timeticks: (11) 0:00:00.11

SNMPv2-MIB::sysORID.1 = OID: UDP-MIB::udpMIB

SNMPv2-MIB::sysORID.2 = OID: SNMPv2-MIB::snmpMIB

SNMPv2-MIB::sysORID.3 = OID: SNMP-VIEW-BASED-ACM-MIB::vacmBasicGroup

[root@vm-vol-nag4-tst servers]#

[root@vm-vol-nag4-tst servers]# snmpwalk -v 1 -c tcspub_123 172.18.98.4 . | head

SNMPv2-MIB::sysDescr.0 = STRING: Linux PowerXpert-00-20-85-F1-4E-54 3.2.2 #1 PREEMPT Wed Oct 14 09:39:43 CEST 2015 ppc

SNMPv2-MIB::sysObjectID.0 = OID: SNMPv2-SMI::enterprises.534.2.12

DISMAN-EVENT-MIB::sysUpTimeInstance = Timeticks: (743) 0:00:07.43

SNMPv2-MIB::sysContact.0 = STRING: Moroz

SNMPv2-MIB::sysName.0 = STRING: PowerXpert-00-20-85-F1-4E-54

SNMPv2-MIB::sysLocation.0 = STRING: MSK Polkovaya 2 Floor 4

SNMPv2-MIB::sysORLastChange.0 = Timeticks: (58) 0:00:00.58

SNMPv2-MIB::sysORID.1 = OID: UDP-MIB::udpMIB

SNMPv2-MIB::sysORID.2 = OID: SNMPv2-MIB::snmpMIB

SNMPv2-MIB::sysORID.3 = OID: SNMP-VIEW-BASED-ACM-MIB::vacmBasicGroup

[root@vm-vol-nag4-tst servers]#

[root@vm-vol-nag4-tst objects]# cat ups/PL-01-UPS1-Eaton.cfg

define host{

use                     ups-server

host_name               PL-01-UPS1-Eaton

address                 172.18.98.2

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     VAN INPUT

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.3.4.1.2.1 -C tcspub_123  -c200:

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     VBN INPUT

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.3.4.1.2.2 -C tcspub_123  -c200:

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     VCN INPUT

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.3.4.1.2.3 -C tcspub_123  -c200:

}

define service{                                                                                                                                                                                                [31/261]

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     VAN Bypass

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.5.3.1.2.3 -C tcspub_123  -c200:

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     VBN Bypass

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.5.3.1.2.2 -C tcspub_123  -c200:

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     VCN Bypass

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.5.3.1.2.1 -C tcspub_123  -c200:

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     Battery run time in seconds

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.2.1.0 -C tcspub_123  -c4000: -usec.

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     Battery charge in percent

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.2.4.0 -C tcspub_123  -w50: -c10: -u%

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     UPS Battery test status

check_command           check_snmp!-o .1.3.6.1.4.1.534.1.8.2.0 -C tcspub_123 -P 1 -c2:2 -u": 2 - passed| 3 - failed| 4 - inProgress| 5 - notSupported| 6 - inhibited| 7 - scheduled"

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     UPS Output Power percent

check_command           check_snmp!-o enterprises.534.1.4.1.0 -C tcspub_123 -P 1 -u"%"

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     UPS Output Power line 1 watts

check_command           check_snmp!-o enterprises.534.1.4.4.1.4.1 -C tcspub_123 -P 1 -u"w"

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     UPS Output Power line 2 watts

check_command           check_snmp!-o enterprises.534.1.4.4.1.4.2 -C tcspub_123 -P 1 -u"w"

}

define service{

use                     generic-service

host_name               PL-01-UPS1-Eaton

service_description     UPS Output Power line 3 watts

check_command           check_snmp!-o enterprises.534.1.4.4.1.4.3 -C tcspub_123 -P 1 -u"w"

}

[root@vm-vol-nag4-tst objects]#